## Slide 1: RESPONSIBILITIES
Slide 3 - 1
S-211
Portable Pumps and Water Use
Unit 3 - Responsibilities
Unit 3

## Slide 2: Words of Experience
Click icon to hear firefighter story about pumps.

## Slide 3: Objectives
Given scenarios and photos, identify risk management, fuel handing, and environmental concerns.
Identify methods to prevent cavitation and water hammer.
List the four components that should be included in the design of a portable water delivery system.
Given photos, critique a portable pump setup.

## Slide 4: Objectives
  Identify how to prevent the engine from flooding when starting the pump.
  Identify how to troubleshoot common problems with portable pumps.
  Identify how to select nozzles and apply water to achieve tactical objectives.
  List general guidelines for maintaining and retrieving hoses.

## Slide 5: General Responsibilities

## Slide 6: Risk Management
Always wear PPE; keep sleeves down.

## Slide 7: Risk Management
Always wear PPE; keep sleeves down.
Ensure LCES is established and known.

## Slide 8: Risk Management
Always wear PPE; keep sleeves down.
Ensure LCES is established and known.
When handling fuel, follow additional safety precautions.

## Slide 9: Risk Management
Always wear PPE; keep sleeves down.
Ensure LCES is established and known.
When handling fuel, follow additional safety precautions.
Follow first aid guidelines.

## Slide 10: Environmental Concerns
  Fuel spills
  Species considerations
  Minimize impact to site
  Rehabilitate site

## Slide 11: Communication
Supervisor
Pump operator
Nozzle operator
Hand crew or other fireline personnel

## Slide 12: Communication Methods

## Slide 13: Cavitation
Definition: When cavities or bubbles form in the water in the low pressure (suction side) of the pump, causing deep pits in the surface of the impeller

## Slide 14: Cavitation
Causes
  Restricted water flow
  Air entering suction hose
  Suction hose diameter too big or too small
  Downhill hose lay with extreme water demand
  High-altitude pumping
What are symptoms that cavitation is occurring?

## Slide 15: Prevent Cavitation
Keep strainer clean and free of debris.
Locate pump as close to water source as practical.
Ensure adequate water supply.
Ensure diameter of suction hose is accurate.

## Slide 16: Water Hammer
Occurs when flowing water is suddenly stopped, resulting in shock waves traveling back the length of hose at high speeds, producing rapid vibrations.

## Slide 17: Water Hammer
Cause
  Valves or nozzles closed suddenly at end of line
  Vehicle driven over hose
What are symptoms that water hammer is occurring or has occurred?

## Slide 18: Prevent Water Hammer
Slowly close valves and nozzles.
Keep nozzles slightly cracked open at all times.
Protect hoses from being driven over.

## Slide 19: Exercise
Pump Accident Investigation Report

## Slide 20: Design Responsibilities

## Slide 21: Design Responsibilities

## Slide 22: Design Responsibilities

## Slide 23: Design Responsibilities
Incorporate these components into the design:
  Portable pump configurations
  Hose lay design
  Nozzle type(s)
  Hydraulic calculations

## Slide 27: Hydraulic Calculations

## Slide 28: Portable Pump Responsibilities

## Slide 29
Slide 3 - 29
S-211
Portable Pumps and Water Use
Unit 3 - Responsibilities

## Slide 31: Portable Pump Responsibilities
Obtain equipment and supplies.
Set up and prime pump; connect hoses.
Mix gas and oil, and refuel.
Start pump.
Operate and maintain pump.
Shut down pump.
Troubleshoot.

## Slide 32: Obtain Equipment and Supplies

## Slide 33: Set Up Pump, Connect Hoses, and Prime Pump
Select a site.
Unpack kit; inventory and inspect.

## Slide 34: Set Up Pump, Connect Hoses, and Prime Pump
Set up containment berms.
Place pump in one berm and fuel can in the other berm.

## Slide 35: Set Up Pump, Connect Hoses, and Prime Pump
Secure pump and fuel can.

## Slide 36: Set Up Pump, Connect Hoses, and Prime Pump
Connect foot valve/strainer to suction hose; fill with water; connect to pump.
Place foot valve at least 1 foot under water; keep strainer clean and free of debris.

## Slide 37: Set Up Pump, Connect Hoses, and Prime Pump
Prime the pump using a hand primer or by filling with water from a pail

## Slide 38: Set Up Pump, Connect Hoses, and Prime Pump
Connect hose curl (pigtail) to discharge side of pump and the other end of hose curl to check and bleeder valve.

## Slide 39: Mix Gas and Oil, and Refuel

## Slide 40: Safety Procedures When Working With Fuel
  ALWAYS wear eye protection and gloves.
  ALWAYS shut the pump down before opening the fuel tank.
  Never operate a radio, cell phone, or other portable device when working with fuel.

## Slide 41: Fuel and Environmental Concerns
  Pumps and fuel cans often leak.
    ALWAYS use containment berms and absorbent pads.
    ALWAYS mix fuel over the containment berm.
  If spill occurs:
    Contain the spill.
    Ensure no more fuel is spilled.
    Notify supervisor, Resource Advisor, or both, immediately.
  If fuel has to be transported or stored, follow agency policy.

## Slide 42
All two cycle pumps require UNLEADED GAS mixed with TWO CYCLE OIL.

## Slide 43: Is fuel pre-mixed?
Pre-mixed fuel (yellow tag)
  Fuel color – red or greenish
  Slippery to touch
Regular gas(red tag)
  Gas color – straw or has no color (clear)
  Needs to be mixed with two cycle oil

## Slide 44: Fuel Mixing Instructions
24:1 Ratio
(5 gal gas: 1 qt oil)
Mix gas and oil.
Shake, and add remaining gas.
1
2
3

## Slide 45: Mix Fuel and Refuel
Write on the appropriate tag the date fuel was mixed, and attach tag to the fuel can.
Attach fuel line to pump-adapted can.
Replace pads; dispose according to agency protocol.

## Slide 46: Start Pump
Tell nozzle operator the pump is ready to start.
Open air vent on fuel can.

## Slide 47: Start Pump
Warm engine:
Choke in run position.
Throttle in start/warm up position.
Cold engine:
Choke in start position.
Throttle in start/warm up position.

## Slide 48: Start Pump
Slowly pump fuel bulb until fuel mixture (in clear fuel tube) is just touching bottom of carburetor.

## Slide 49: Start Pump
Immediately set choke lever to run position.
Turn switch on (if there is a switch).
On Mark 3 pump, ensure overspeed reset rod is pushed in.
Pull starter rope with short, quick pulls (2 to 4 pulls) until engine “pops.”
Click icon to hear engine pop.

## Slide 50: Start Pump
  Pull starter rope 1 to 3 more times, and the pump engine should start.
  Additional pulls of rope with choke in start position (after engine pops) will flood engine.
  Allow engine 2 minutes to warm up before moving throttle to run position.

## Slide 51: Operate and Maintain Pump
Prevent pump cavitation and water hammer.
Ensure water is flowing through pump head at all times. Crack nozzle open or open bleeder valve.

## Slide 52: Operate and Maintain Pump
Tighten loose nuts and bolts.
Grease pump head.

## Slide 53: Operate Pump
Listen to pump
  Lugging
  Rapid rpms
  Sputtering
Click on the sound icon to play audio.

## Slide 54: Sputter
Sputtering may indicate a carburetor problem.
Significant elevation change may cause carburetor to not work correctly (fuel/air mixture problems).

## Slide 55: Pump Carburetor Adjustment
CONSULT WITH YOUR SUPERVISOR OR FOLLOW LOCAL POLICY, OR BOTH REGARDING ADJUSTMENT OF CARBURETOR.

## Slide 56: Do not adjust the low idle screw.
Click the screen to play the video clip.
    When pump’s engine is warm, run at full throttle.
    Slowly turn high idle screw until maximum rpm is reached and passed.
    Turn high idle screw the opposite direction until maximum rpm is reached again.
    Turn screw counter clockwise ¼ of a turn to obtain both maximum rpm and proper engine lubrication.

## Slide 57: Shutdown Pump
Communicate with nozzle operator.
Move throttle lever to “stop” position.
Drain fuel line.
Drain pump head (in freezing conditions).
1
2
3
4

## Slide 58: Troubleshooting Pump Problems
Click the video window to play the video clip.

## Slide 59: Troubleshooting – Symptoms and Remedies

## Slide 60: Troubleshooting – Symptoms and Remedies

## Slide 61: Troubleshooting – Symptoms and Remedies

## Slide 62: Troubleshooting – Symptoms and Remedies

## Slide 63: Troubleshoot: Step-by-Step Process Using the IRPG

## Slide 64
Slide 3 - 64
S-211
Portable Pumps and Water Use
Unit 3 - Responsibilities

## Slide 65: Troubleshooting – Check Air Filter
1
2
3
4
5

## Slide 66: Troubleshooting – Broken Starter Assembly
Remove starter housing.
Wrap piece of rope or cord around starter assembly, and pull to start pump.
1
2

## Slide 67: Identify Problems With Flagging

## Slide 68: nozzle responsibilities

## Slide 69
Select Nozzle(s)
Twin tip nozzles
Adjustable barrel nozzles
Sprinklers

## Slide 70: Apply Water
Straight stream
Fire too hot to get close
Fire confined to small area
Reach long distance (snags, treetops, hot roots or beds)
Fog or spray
Hot spotting, wet lining, direct attack, mop up
Close work
Fire covers large area
Smaller volume of water is required
Slide 3 - 70

## Slide 71: Guidelines for Applying Water
Approach fire with charged hose.
Aim at base of flame and use sweeping motion.

## Slide 72: Guidelines for Applying Water
Avoid excessive water pressure.
Watch for flare-ups.
Conserve water.

## Slide 73: Straight stream or fog/spray?
1
2
3
4

## Slide 74
Open and close nozzles slowly to prevent water hammer.
Operation and Maintenance

## Slide 75: Operation and Maintenance
Unclog nozzle tips.

## Slide 76: Communication
Communicate up and down the hose lay to know how many nozzles can be open at a time.
  Hose lay may have 15 laterals, but pump can only support 3 or 4 nozzles being open simultaneously.

## Slide 77: Hose Lay Responsibilities

## Slide 78: Set Up Hose Lay – Simple Hose Lay

## Slide 79: Set Up Hose Lay – Progressive Hose Lay

## Slide 80: Maintain and Retrieve Hose Lay
Replace protective caps on accessories and male hose ends.
Replace broken hose and check for kinked hose.

## Slide 81
Keep hose line out of hot spots.
Use accepted method of rolling hose.
Properly store hose in a safe location.
Maintain and Retrieve Hose Lay

## Slide 82: Setting up Multiple pump systems

## Slide 83: Series Pumping
Set up Pump 1.
Set up Pump 2.
Double check all appliances.
Start Pump 1.
Start Pump 2.
Monitor fuel levels.
Shut down:
  Open check and bleeder on Pump 2.
  Slow down Pump 2 to idle.
  Slow down Pump 1 to idle.
  After pumps cooled down, turn them off.

## Slide 84: Parallel Pumping
Set up two pumps.
Either pump may be started or stopped at any time.
Monitor fuel levels.
Shut down:
  Slow down to idle speed to cool off.
  Turn off.

## Slide 85: Staged Pumping
Setup, operation, and shutdown are the same as using one pump.

## Slide 86: Chemicals

## Slide 87: Review

## Slide 88: Review
1. There is a fuel spill. What should you do?
Answer:
Contain the spill.
Ensure no more fuel is spilled.
Notify supervisor or resource advisor immediately.

## Slide 89: Review
What are some risk management issues specific to operating a portable pump and hose lay?
Possible answers:
  Wear full PPE
      Pump operator needs to wear eye, ear, and hand protection.
      Nozzle operator needs to wear eye and hand protection.
  Ensure LCES is established and known. Nozzle operator at high risk of injury.
  Fuel handling requires additional safety precautions (i.e., no talking on the radio or cell phone).
  Follow first aid guidelines.

## Slide 90: Review
What are the four components that should be included in the design of a delivery system?
Possible answers:
  Pump configuration
  Hose lay design
  Nozzle type
  Hydraulic calculations, as appropriate

## Slide 91: Review
Critique this pump set up:
Possible answers:
  Pump and fuel can in one berm; should be in separate berms.
  Pump and fuel can are not secured.
  Muffler on pump facing fuel can.

## Slide 92: Review
When fueling or refueling, what are safety procedures the pump operator should follow?
Possible answers:
  Wear full PPE, including eye, and hand protection.
  When pouring fuel or mixing gas with oil, do it over a containment berm.
  Shut down pump before opening fuel can (i.e., to check fuel level).
  Never operate a radio or electronic device when working with fuel.

## Slide 93: Review
When you start the pump, what can you do to prevent flooding the engine?
Possible answer:
  After engine “pops,” don’t pull rope with choke in start position.

## Slide 94: Review
You hear the pump lugging; what could be the problem?
Possible answer:
  Pump is running out of fuel.
  Nozzle shut down.
  Hydraulic or mechanical problems.

## Slide 95: Review
You hear the pump having rapid rpms. What could be the problem?
Possible answer:
  Pump lost its prime.
  Broken discharge hose.
  Broken suction hose.
  Open nozzle.

## Slide 96: Review
What could cause the pump to lose its prime?
Answer:
  Suction hose connections are leaking.
  Suction hose is defective.
  Priming cap is loose.
  Foot valve not fully submerged in water source.

## Slide 97: Review
What can a pump operator do to prevent pump cavitation?
Answer:
  Keep strainer clean and free of debris.
  Locate pump as close to water source as practical.
  Ensure adequate water supply.
  Ensure diameter of suction hose is accurate.

## Slide 98: Review
What can a pump and nozzle operator do to prevent water hammer?
Answer:
  Slowly close valves and nozzles.
  Slightly crack open nozzles at all times.
  Protect hoses from being driven over.

## Slide 99: Review
In what situations would it be advantageous for the nozzle operator to use the straight stream?
Answer
  Fire is too hot to get close.
  Fire is confined to small area.
  A lot of pressure is needed to reach long distance (snags, tree tops, hot roots or beds).

## Slide 100: Review
In what situations would it be advantageous for the nozzle operator to use the fog/spray?
Answer:
  Hot spotting, wet lining, direct attack, and mop up.
  Close work is needed.
  Fire covers a larger area.
  A smaller volume of water is required to put out the fire or water conservation is necessary.

## Slide 101: Review
What are some general guidelines for applying water?
Answer:
  Approach fire with charged hose.
  Aim at base of flame and maintain water stream in sweeping motion.
  Avoid excessive water pressure.
  Conserve water.
  Watch for flare-ups.

## Slide 102: Review
What are some general guidelines for maintaining and retrieving hoses?
Answer:
  Replace protective caps on accessories and male hose ends.
  Be sure female ends have a gasket.
  Replace broken hose.
  Check for kinked hose.
  Keep hose line out of hot spots.
  Use accepted method of rolling hose when retrieving.
  Properly store hose in a safe location.

## Slide 103: Objectives
Given scenarios and photos, identify risk management, fuel handing, and environmental concerns.
Identify methods to prevent cavitation and water hammer.
List the four components that should be included in the design of a portable water delivery system.
Given photos, critique a portable pump setup.

## Slide 104: Objectives
  Identify how to prevent the engine from flooding when starting the pump.
  Identify how to troubleshoot common problems with portable pumps.
  Identify how to select nozzles and apply water to achieve tactical objectives.
  List general guidelines for maintaining and retrieving hoses.