## Slide 1: Equipment Description
Notes: The Electric Utility System is much more than just Generation facilities, Towers, Poles, Lines, and Substations. At each of these locations there must be ancillary equipment that helps attach the lines to the towers, poles, and substations; equipment to protect the systems from shorting, overloading, and adjusting the levels of electric current throughout the system.

## Slide 2
Objective
Describe the Typical Electric Utility Ancillary Equipment, their Primary Function, and their Potential Faulting and Failures.
Notes: This section will provide you with the basic understanding of the types of equipment used throughout the system and how the function. In addition, the standard operation of many of these devises may generate potential ignition sources and should not be considered as a “failure” on the equipment’s function. However, electrical equipment can “fail” to function properly when if it is installed improperly, is not properly maintained or it is subjected to conditions outside the normal range of operations.

## Slide 3
Ancillary Equipment
Fuses
Cutouts
Disconnects
Lightning Arresters
Hot Tap Clamps
Split Bolt Connectors
Miscellaneous Connectors
Air Switches
Reclosers
Sectionalizers
Voltage Regulators
Capacitor Banks
Transformers
Parallel Grove Connectors
Piercing Tap Clamps Wedge Connectors
Compression Connectors
Flat Plate Connectors
Automatic Deadends
Splices
Insulators
Notes: Most equipment can be categorized into these general areas. Depending on the style, type, and components when operating properly the item may generate moderate to large quantities of ignition source materiel or may not generate any. Those that are known to generate ignition source materiel are classified as “Non-Exempt” in many areas and will require the application special clearance and maintenance requirements. Those that do not normally generate sources of ignition when operating properly are classified as “Exempt” and are not normally subject to the same requirements as “Non-Exempt”. However, the Fire Investigator must be aware that even though the types of equipment in the Area of Origin are classified an “Exempt”, they may have generated the source of ignition and their classification should not be mistaken as excluding them from consideration.

## Slide 4
Universal Fuse
Non-Exempt
Expulsion end of fuse
Pull Ring
Notes: When functioning properly, the heating and breaking of the fuse will drop out hot molten materiel that would be expelled from the bottom of the fuse and may be an ignition source. The Fire Investigator may find melted pieces of the fuse or parts of the expelled materiel. If contact is made by a foreign object between the upper and lower portions of the fuse or fuse holder a failure can occur.

## Slide 5
Universal Fuse
Non-Exempt
Arm Mounted Cutout with Universal Fuse

## Slide 6
Open Link Fuse
Non-Exempt
Arm Mounted Cutout with Open Link Fuse
Notes: When functioning properly, the heating and breaking of the fuse will drop out hot molten materiel that would be thrown from the fuse and may be an ignition source. The Fire Investigator may find melted pieces of the fuse or parts of the expelled materiel.

## Slide 7
Bushing Mounted Cutout with Open Link Fuses
Open Link Fuse
Non-Exempt

## Slide 8
Enclosed Cutouts with Universal Fuse
Non-Exempt

## Slide 9
Solid Blade Disconnect
Non-Exempt
Solid Blade Disconnect - Closed
Solid Blade Disconnect - Open
Notes: When moving from the closed to open position there is the potential for an electrical arch that may produce hot molten materiel that may be an ignition source. The Fire Investigator may find molten pieces of metal and would need to exam the blades to determine if they had been damaged and were a sources of the materiel.

## Slide 10
Solid Blade Disconnect
Non-Exempt
600 amp disconnect
4 kV Bayonet
Notes: Note: Solid Blade Disconnects are considered “Exempt” when used in conjunction with Reclosers, Sectionalizers, and Voltage Regulators. However, they may still expel materiel.

## Slide 11
Combination
Non-Exempt and Exempt Hardware
Solid Blade Disconnect in
Open Position – Non-Exempt
Arm Mounted Cutout with Non-Expulsion Fuse - Exempt

## Slide 12
In-Line Disconnect
Non-Exempt
Notes: When moving from the closed to open position there is the potential for an electrical arch that may produce hot molten materiel that may be an ignition source. The Fire Investigator may find molten pieces of metal and would need to exam the blades to determine if they had been damaged and were a sources of the materiel.

## Slide 13
In-Line Disconnect
Non-Exempt

## Slide 14
Lightning Arrestors
Non-Exempt
Arm Mounted Lightning Arrestors with Cable Riser and Universal Fuses
Lightning Arrestors
with Recloser
Notes: When functioning properly, the lightning arrestor may drop out hot molten materiel springs or parts from the bottom of the arrestor and may be an ignition source. The Fire Investigator may find melted pieces of the arrestor or parts of the expelled materiel. If contact is made by a foreign object between the upper and lower portions of the arrestor a failure can occur.

## Slide 15
Lightning Arrestors
Non-Exempt

## Slide 16
Non-Porcelain Lightning Arrestors
Non-Exempt

## Slide 17
Lightning Arrestors
Non-Exempt
Lightning Arrestors
with Transformer
Gapped Lightning Arrestor

## Slide 18
Lightning Arrestors
Non-Exempt

## Slide 19
Hot Tap Clamps
Non-Exempt
Notes: Note: These types of Hot Tap Clamps are “Non-Exempt”. Other types of Hot Tap Clamps shown later are “Exempt”. Those have mechanisms that maintain pressure on the clamping device to avoid slippage and arching. The Fire Investigator may find molten pieces of metal and would need to exam the clamps and the line to determine if they had been damaged and were a sources of the molten materiel.

## Slide 20
Split Bolt Connectors
Non-Exempt
Idle Split Bolt
Notes: Note: Split Bolt Connectors used in this configuration are “Non-Exempt”. If shown in an “Idle Position” , that is the Split Bolt is connected to one line but the other line is not connected to any line. Equipment or other hardware it is “Exempt”. The Fire Investigator may find molten pieces of metal and would need to exam the connectors and the line to determine if they had been damaged and were a sources of the molten materiel.

## Slide 21
Miscellaneous Connectors
Non-Exempt
Fargo Connectors
LM Connector

## Slide 22
Grasshopper Air Switch
Non-Exempt
Closed
Open
Notes: When operating normally, the action of moving from the closed to open position may establish an arch between the blades that may expel molten materiel that may be an ignition source. The Fire Investigator may find molten pieces of metal and would need to exam the blades and the connecting points to determine if it had been damaged and was a source of the molten materiel.

## Slide 23
Transmission Air Switch
Non-Exempt
Notes: When operating normally, the action of moving from the closed to open position may establish an arch between the blades that may expel molten materiel that may be an ignition source. The Fire Investigator may find molten pieces of metal and would need to exam the blades and connecting points to determine if it had been damaged and was a source of the molten materiel.

## Slide 24
Transmission Air Switch
Non-Exempt

## Slide 25
Non-Expulsion Fuses
Exempt

## Slide 26
Non-Expulsion Fuses
Exempt

## Slide 27
Liquid Filled Fuses
Exempt

## Slide 28
Liquid Filled Fuses
Exempt

## Slide 29
SMU-20 Fuses
Exempt

## Slide 30
SMU-20 Fuses
Exempt
Lightning Arrestors
Non-Exempt

## Slide 31
S&C Fault Tamer Fuses
Exempt

## Slide 32
600 Amp KPF Air Switch
Exempt
Triangular Construction – Open and Closed Positions
Notes: Although these Air Switches operate similar to those that are “Non-Exempt” the metal “whip-like tail” that can be seen in the open position minimizes the arching potential and molten metal development.

## Slide 33
600 Amp KPF Air Switch
Exempt
Crossarm Construction – Closed Position

## Slide 34
Underarm Sidebreak Switch
Exempt
Open Position

## Slide 35
Closed Position
Underarm Sidebreak Switch
Exempt

## Slide 36
S&C Underarm Side-break Switch
Exempt
Closed Position

## Slide 37
S&C Omni-Ruptor Switch
Exempt
Closed Position
Open Position

## Slide 38
S&C Scada-Mate Switch
Exempt
Open Position - Green
Closed Position - Red

## Slide 39
In-Line Disconnects
Recloser
Exempt
Solid Blade Disconnects
Notes: Solid Blade and In-Line Disconnects are considered “Exempt” when used in conjunction with Reclosers, Sectionalizers, and Voltage Regulators. However, they may still expel materiel.

## Slide 40
Sectionalizer
Exempt

## Slide 41
Voltage Regulators
Exempt

## Slide 42
Capacitor Bank
Exempt

## Slide 43
Transformers
Exempt

## Slide 44
Parallel Groove Connectors
Exempt

## Slide 45
Hot Tap Clamps
Exempt
Notes: Note the “Ears” on the bottom of the Exempt Hot Tap Clamp. The “Non-Exempt” Hot Tap Clamps do NOT have the “Ears”.

## Slide 46
Piercing Hot Tap Clamp
Exempt
Piercing Clamp on Tree Wire

## Slide 47
Wedge Connectors
Exempt

## Slide 48
Compression & Bolted Flat Plate Connectors
Exempt

## Slide 49
Splices
Exempt
Notes: Note: Splices may be installed on lines that have been weakened by line to line or contact that caused arching and dropped molten metal as an ignition source or tree to line contact that was an ignition source for a wildfire. The splices will cover the pit marks and make the identification of the evidence difficult. Once in place the splices are difficult to remove. For the Fire Investigator, the discovery of freshly installed splices within the area of origin, may require additional evidence gathering that may include obtaining the section of the line in question.

## Slide 50
Animal Protection Devices
Raptor Perch - Birds
Insulated Conductor Covering
Birds – Squirrels - Cats

## Slide 51
Animal Protection Devices
Anti-Perch Guard
Anti-Perch Owl

## Slide 52
Animal Protection Devices
Squirrels Guards

## Slide 53
Circuit Protection Devices
Vibration Dampers
Vibration Dampers
Line Opener
Long Span Conductor Spreader

## Slide 54
Insulators
Notes: Insulator failures are common when they are not maintained. Age may warp the holes hold the insulator seating pin and cause arching. Dirt, moisture, bird drops may negate the insulating properties and cause a short, arching, and insulator failure.

## Slide 55
Knowledge Check
Which of the following pieces of electrical ancillary equipment is classified as “Non-Exempt”:
  Piercing Hot Tap Clamp
  Universal Fuse
  SMU-20 Fuse
  Transformer
Notes: The correct answer is B. A Universal Fuse will expel hot molten materiel from the expulsion port of the fuse.

## Slide 56
Knowledge Check
Which item of electrical ancillary equipment is always classified as “Non-Exempt :
  Hot Tap Clamps
  Split Bolt Connectors
  Solid Blade Disconnects
  Grasshopper Air Switches
Notes: The correct answer is D. The Grasshopper Air Switch. The others may be classified as “Exempt”: Hot Tap Clamps are Exempt if fitted with a spring type locking mechanism (Clamp will have “ears” on the end of the fitting); Split Bolt Connectors are Exempt if they are in an idle position; and Solid Blade Disconnect are Exempt if they are used in conjunction with a Recloser, Voltage Regulator, or Sectionalizers.

## Slide 57
Knowledge Check
“Exempt” hardware can be an ignition source for Wildfires:
True
False
Notes: The correct answer is True. The Fire Investigator should not discount those ancillary electric equipment because they are classified as “Exempt”.